## Kearsley
KEARSLEY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - JANUARY 2020
|  | Environment Protection Licence No. 3232 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 3 February 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 20 February 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Discharge from No.2 Oxidation Pond
Site Code 5SL2600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 January 2020 to 31 January 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 13 | 63.2 | 17 | 208 | N/A | N/A | 60 | 208 | Yes*
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 5 | 28.6 | 6238.24 | 205 | 19800 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.4 | 5.4 | 5.4 | 5.4 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 10.75 | 10.75 | 10.75 | 10.75 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 5 | 7.23 | 7.976 | 7.89 | 9 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.7 | 5.7 | 5.7 | 5.7 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 5 | 22 | 1079.8 | 39 | 3330 | N/A | N/A | 70 | 3330 | Yes*
*The licensee is not taken to have exceeded a quality limit specified in this licence for pH, BOD or TSS if the licensee shows that the level of chlorophyll-a in the oxidation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by excessive algal growth).
VOLUME MONITORING |  |  | 31
Monthly Summary
1 January 2020 to 31 January 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 1 - Discharge from No.2 Oxidation Pond |  |  | 7 | kilolitres per day | 0.19912 | Daily | 31 |  | 199.116 | 2500 | Yes
Chlorophyll 'a'
Chlorophyll 'a'
Note on D26: awebb: Last row of flow table