## Kearsley
KEARSLEY WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2019-2020
| Environment Protection Licence No. 3232 | [7 empty] | Licensee | Hunter Water Corporation
| Date Obtained: 1 April 2020 | [8 empty] | 36 Honeysuckle Drive
| Date Published: 23 April 2020 | [8 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Discharge from No.2 Oxidation Pond
Site Code 5SL2600
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 April 2019 to 31 March 2020
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
pH | pH | Weekly | 52 | 7.23 | 9.81 | N/A | N/A | 6.5 - 8.5 | 7.64 - 9.48 | N/A | N/A | N/A | N/A | Yes*
Biochemical Oxygen Demand | milligrams per litre | Weekly | 52 | 2 | 208 | 30 | 17 | 50 | 63 | N/A | N/A | 60 | 208 | Yes*
Total Suspended Solids | milligrams per litre | Weekly | 52 | 1 | 3330 | 50 | 38 | 55 | 258 | N/A | N/A | 70 | 3330 | No**
Chlorophyll a | micrograms per litre | Weekly | 52 | 1.9 | 20200 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | 0.05 | 21 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | milligrams per litre | Monthly | 12 | 6.05 | 219.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Oil and Grease | milligrams per litre | Monthly | 12 | <2 | 9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | Monthly | 12 | 2.9 | 17.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
*The licensee is not taken to have exceeded a quality limit specified in this licence for pH, BOD or TSS if the licensee shows that the level of chlorophyll-a in the oxidation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by excessive algal growth).
**The total suspended solids 100%ile limit was breached whilst Chlorophyll a was less than 100 ug/L. 50%ile and 90%ile limits were not breached.
VOLUME MONITORING
Annual Summary
1 April 2019 to 31 March 2020
Monitoring Point |  |  | Unit of | Sampling | No. of times measured during the year |  |  | Volume | Within
|  |  | Measurement | Frequency |  |  | Maximum | Limit | Limits?
Point 1 - Discharge from No.2 Oxidation Pond |  |  | kilolitres per day | Daily | 366 |  | 1587 | 2500 | Yes