## Tanilba Bay
TANILBA BAY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - MARCH 2020
|  | Environment Protection Licence No. 4435 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 1 April 2020 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 23 April 2020 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - Immediately downstream of the UV disinfection system
Site Code 5SL2900
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 March 2020 to 31 March 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <2 | 2.5 | <2 | 4 | N/A | N/A | 30 | 4 | Yes
Conductivity | Cond | microsiemens per centimetre | (µS/cm) | Monthly | MONTHLY | 1 | 572 | 572 | 572 | 572 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.2 | 0.2 | 0.2 | 0.2 | N/A | N/A | 5 | 0.2 | Yes
Nitrate + Nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 4.4 | 4.4 | 4.4 | 4.4 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.6 | 5.6 | 5.6 | 5.6 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Fortnightly | FORTNIGHTLY | 2 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 3.9 | 3.9 | 3.9 | 3.9 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | <1 | <1 | <1 | <1 | N/A | N/A | 50 | <1 | Yes
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.24 | 7.3725 | 7.415 | 7.42 | N/A | N/A | 6.5 - 8.5 | 7.24 - 7.42 | Yes
EPA Id. No. 3 |  | Site Description - Emergency Overflow from Infiltration Pond No.4
Site Code 5OV2900
[6 empty] | No. of times measured during the month for licence reporting # | Monthly Summary
1 March 2020 to 31 March 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Each Overflow Event |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
# No samples were collected as no discharge occurred during the month
EPA Id. No. 17 |  | Site Description - Infiltration Pond 1
Site Code 54Z3013
[6 empty] | No. of times measured during the month for licence reporting* | Monthly Summary
1 March 2020 to 31 March 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
*Sample not collected as Infiltration Pond 1 was dry.
EPA Id. No. 18 |  | Site Description - Infiltration Pond 2
Site Code 54Z3014
[6 empty] | No. of times measured during the month for licence reporting** | Monthly Summary
1 March 2020 to 31 March 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
**Sample not collected as Infiltration Pond 2 was dry.
EPA Id. No. 19 |  | Site Description - Infiltration Pond 3
Site Code 54Z3015
[6 empty] | No. of times measured during the month for licence reporting*** | Monthly Summary
1 March 2020 to 31 March 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
***Sample not collected as Infiltration Pond 3 was dry.
EPA Id. No. 20 |  | Site Description - Infiltration Pond 4
Site Code 54Z3016
[6 empty] | No. of times measured during the month for licence reporting **** | Monthly Summary
1 March 2020 to 31 March 2020
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Conductivity | Conductivity | microsiemens per centimetre | (µS/cm) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | FC Hdn | colony forming units per 100 mL | CFU/100mL | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrate + nitrite (oxidised nitrogen) | TON | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Quarterly |  | - | - | - | - | - | N/A | N/A | N/A | N/A | N/A
****Sample not collected as Infiltration Pond 4 was dry.
VOLUME MONITORING |  |  | 117
Monthly Summary
1 March 2020 to 31 March 2020
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  |  | Volume | Within Limits
|  |  |  | Measurement |  | Frequency |  |  | Maximum | Limit
Point 2 - Effluent Flume Channel |  |  | 4 | kilolitres per day | 1.88 | Daily | 31 |  | 1880 | 10000 | Yes
Note on D112: awebb: Last row of flow table